## Slide 1: WinSLAMM v 10 Catchbasins/ Hydrodynamic Devices
Using WinSLAMM v10 to Meet Urban Stormwater Management Goals

## Slide 2: We will cover . . .
Research Results
Entering Catchbasin Data into the Model
Model Output
Variable Sensitivity

## Slide 3: Catchbasins

## Slide 4: Research Results
A New Jersey study (Pitt, et al, 1994) found average removal rates of 32% for suspended solids using catchbasins with a suitable sump.
Pitt & Shawley (1982) found cleaning catchbasin twice per year reduced total residue yields between 10% and 25%.
Pitt & Field (2004) found sediment in catchbasins were the largest particles washed from streets.
Notes: Pitt, R. and Field, R., Catchbasins and Inserts for the Control of Gross Solids and Conventional Stormwater Pollutants, ASCE World Water and Environmental Resources Congress, Salt Lake City, Utah, June, 2004
Pitt, R. and G. Shawley. A Demonstration of Non-Point Source Pollution Management on Castro Valley Creek. Alameda County Flood Control and Water Conservation District and the U.S. Environmental Protection Agency Water Planning Division (Nationwide Urban Runoff Program). Washington, D.C. June 1982.
Clark, S., R. Pitt, and R. Field. “Stormwater Treatment Using Inlet Devices, Filter Media, and Filter Fabrics.” In: Proceedings of the Engineering Foundation Conference: Stormwater NPDES Related Monitoring Needs. Edited by H.C. Torno. Engineering Foundation and ASCE. New York, NY. 1994. pp. 641 – 650.

## Slide 5: Catchbasins . . .
Are Inlets or Manholes
Must Contain a Sump
Are not very useful if streets are also swept
Are applied as drainage controls
Notes: The particulates removed by street sweeping and the particulates removed by catchbasin are typically composed of the same particle sizes. To prevent an inaccurate increase in the reduction in sediment removal because of this, the model will not route the remaining sediment from those streets that are swept to the catchbasin if both practices are modeled together.

## Slide 6
Effect of Drainage System Configuration
Manholes
Parallel Collection System
Inlets with Sumps
Series Collection System
Collection System | # CBs | % TSS Reduction
Parallel | 11 | 11.16%
Series | 11 | 8.91%
Notes: Catchbasins cannot be modeled in series in one file because the incremental increase in flow in each basin will not be reflected in the model. To evaluate a system in series, create additional files for each catchbasin in series. In each file, create two sets of source areas. The first set will be for the surface drainage to the catchbasin you are modeling. The second set will be for the upstream areas draining to the catchbasin through the pipe. These source areas should have an ‘Other Control’ device with the particulate solids loading set to zero. This will remove the upstream solids from the model run yet still allow the device to be evaluated with the correct flow rates, from the entire drainage basin.

## Slide 7: Four Components to Modeling Catchbasins
Device Density
Device Geometry
Flow and Particle Size Data
Device Cleaning Information

## Slide 8
Catchbasin Density
Notes: Catchbasins are assumed to be a part of the drainage system, so the particulate solids reduction is for catchbasins is listed in the Total Area, with Drainage and Outfall Controls - Yield of PARTICULATE SOLIDS (lbs) column in the Particulate Solids - Yield tab of the model output. Following this column is a listing of the percent of the total catchbasin volume that is full for each rainfall event. This value is reset to zero based upon either the Catchbasin Cleaning Dates or the Catchbasin Cleaning Frequency entered in the model.
Catchbasins are modeled as vertical walled detention basins with a pipe outlet. However, because they are small, they have negligible storage volume, so the storage component of the detention pond algorithm is ignored. Pipe outlet flow is calculated as the flow rate through a partially filled pipe or as orifice flow, whichever is smaller. The total flow to the catchbasin is divided by the number of catchbasins to determine the flow a typical catchbasin. The NURP.CPZ critical particle size file will usually provide typical catchbasin removal rates.
To model Catchbasin Performance, enter the following information:
1. Area served by catchbasins control (acres).
2a. The catchbasin density (using either typical catchbasin densities provided or enter in your site-specific value), or
2b. The number of catchbasins in the site you are modeling.
3. The Average Sump Depth below the catchbasin outlet invert(ft). Note that the model assumes that the top foot of storage volume is unavailable for storage due to scour. Therefore, the sump depth must be greater than 1.0 ft in order for the catchbasin to function. The catchbasin is considered 100% full when the sump depth less the scour depth is reached.
4. Depth of sediment in catchbasin sump at the beginning of the study period (ft).
5. Typical outlet pipe diameter (ft)
6. Typical outlet pipe Mannings n
7. Typical outlet pipe slope (ft/ft).
8. Typical catchbasin sump surface area (sq. ft)
9. Catchbasin depth from sump bottom to street level (ft). This value should be the sum of the average sump depth, the pipe diameter, the pipe wall thickness, and the typical cover over the pipe from the top of the pipe to the street surface.

## Slide 9
Geometry Information
Use average values for the drainage basin you are modeling
Notes: To evaluate a catchbasin that has an Inflow Bypass Device, select the 'Inflow Bypass Data' button. You will be asked to enter either 1) the maximum flow to the in-line sump or to enter 2) the data needed to determine the flow bypass rate based upon the device geometry.
The 'Inflow Bypass Data' button will be italicized if inflow bypass data has been entered.

## Slide 10: Inflow Bypass Data
Sump Area
Notes: The units for all bypass variables are in feet. Whatever runoff flows through the overflow weir will be untreated, and included as runoff volume after the drainage system. The Overflow Weir is modeled as a sharp-crested weir. A schematic of a catchbasin sump with a bypass flow system is illustrated above.

## Slide 11: Inflow Bypass Data
Two Options – Either User-defined Maximum Flow, or . . .
Notes: If you enter the maximum flow to the in-line sump, then any flows greater than the entered flow rate will be routed around the catchbasin. This water will be untreated, and included as runoff volume after the drainage system.

## Slide 12: Inflow Bypass Data
Defined Flow Diversion Geometry
Lamella Plates or Tube Settlers are also an option
(See Hydrodynamic Device discussion)
Notes: If you elect to have the model calculate the bypass flow rate based upon the model geometry, then you must enter:
a. The diameter of the orifice that controls the flow to the in-line sump.
b. The invert elevation of the orifice that controls the flow to the in-line sump.
c. The length of the overflow, or bypass, structure.
d. The invert elevation of the overflow, or bypass, structure.

## Slide 13
Flow and Particle Size Data
Particle Size Distribution File not accessible if Flows and Particle Sizes transferred through the drainage system
Notes: 10. The inflow hydrograph peak-to-average flow ratio. The default value is 3.8; change it if you have better data.
11. Leakage rate through the sump bottom (in/hr). This value is used to model catchbasins that do not have sealed sumps. However, the impact on catchbasin effectiveness is typically minimal because the sump areas are small.
12. Critical particle size file name. These files are the same format as the .CPZ files used in wet detention ponds.

## Slide 14
Catchbasin Cleaning Information
Notes: To enter catchbasin cleaning dates to model catchbasin cleaning, you can select either:
Catchbasin Cleaning Dates, which are the dates that the catchbasin is cleaned (ie, the % full value is reset to zero) during the study period (cleaning up to 5 times is allowed). The dates must be consecutive, within the study time period, and in the format "MM/DD/YY", or . . .
b. The Catchbasin Cleaning Frequency. The catchbasins will be cleaned (ie, the % full value is reset to zero) at the selected interval. This option is useful for long model runs.
To clear a catchbasin cleaning date, place the cursor on the date, press the right mouse button, and select the 'Clear Date' option (the only one there is).

## Slide 15
Catchbasin Performance
Settling modeled as a detention basin assuming:
  Vertical sides
  No storage
Flow rate calculated using Complex Triangular Hydrograph
Particulate removal based upon particle size
Transition from Stokes (laminar) to Newton (turbulent) Settling Rates

## Slide 16: Additional Output
Catchbasin Performance by Event
Other Output Options
Stage-outflow data
Performance by time step
Stage-inflow data
Notes: StageOutflowCB.csv - Comma separated value file (easily imported into Excel) that lists the stage-discharge relationship for the catchbasin based upon the outlet structures the user enters into the model.
StageInflowCB.csv - Comma separated value file (easily imported into Excel) that lists the stage-inflow relationship for the catchbasin based upon the inflow bypass data the user enters into the model. If there is no inflow bypass, ignore this data.
CBPerformanceByStep.csv - Comma separated value file (easily imported into Excel) that describes the catchbasin performance by time step. This is a very large file.
CBPerformance.csv - Comma separated value file (easily imported into Excel) that describes the catchbasin performance by rainfall event.

## Slide 17: Hydrodynamic Devices

## Slide 18: Research Results
Clark (2006) evaluated the performance of inclined plate settlers for treating stormwater solids
Greb et al (1998) evaluated the performance of a hydrodynamic device in a City of Madison maintenance yard.
Notes: Greb, S., S. Corsi, and R. Waschbusch. 1998. Evaluation of Stormceptor® and multi-chamber treatment train as urban retrofit strategies. In Proceedings: National Conference on Retrofit Opportunities for Water Resource Protection in Urban Environments, Chicago, IL, February 9-12, 1998. U.S. Environmental Protection Agency, Washington, DC
Clark, Shirley, James C. Elligson, J. Bradley Mikula, P.E., Christopher D. Roenning, Julia M. Hafera, and Kelly A. Franklin, “Inclined Plate Settlers to Treat Stormwater Solids”, WEFTEC 2006, Dallas, TX

## Slide 19
General Hydrodynamic Device Information
Notes: Hydrodynamic devices are available for any individual source area. If you want to combine more than one source area, you can model the single chamber device as a catchbasin with inflow bypass data in the drainage system.
There are four sections to the hydrodynamic control device. They are:
1. Hydrodynamic Device General Information. This includes the source area of the device, the area within the source area that is served by the device, the number of devices, the device density and the particle size file name (to define the particle size distribution of the runoff entering the device. This information is needed regardless of whether you are modeling a single chamber device or a proprietary device.
You will also need to enter either the information necessary to characterize a single chamber device or a proprietary device. The single chamber device includes the same information that you would enter for a catchbasin with inflow bypass data. The proprietary device option will allow you to select a particular device manufacturer and model number, assuming the performance data for that device has been added to WinSLAMM.

## Slide 20
Single Chamber Device Characteristics with Maximum Flow to In-Line Sump
Defined Flow Diversion Geometry
Notes: Hydrodynamic devices are available for any individual source area. If you want to combine more than one source area, you can model the single chamber device as a catchbasin with inflow bypass data in the drainage system.
You will also need to enter either the information necessary to characterize a single chamber device or a proprietary device. The single chamber device includes the same information that you would enter for a catchbasin with inflow bypass data. The proprietary device option will allow you to select a particular device manufacturer and model number, assuming the performance data for that device has been added to WinSLAMM.
Single Chamber Device Characteristics. If you are modeling a generic single chamber device, you must enter the following information.
Average sump depth below hydrodynamic device outlet invert (feet)
Depth of sediment in hydrodynamic device sump at beginning of study period (ft)
Typical outlet pipe diameter (ft)
Typical outlet pipe Mannings n
Typical outlet pipe slope (ft/ft)
Typical hydrodynamic device sump surface area (square feet)
Total hydrodynamic device depth (feet)
Inflow hydrograph peak to average flow ratio
Maximum allowable depth of sediment below outlet invert elevation
Either: Maximum flow to inline sump (cfs)
Or: Diameter of orifice that controls flow to in-line sump (ft)
Inflow orifice invert elevation (ft)
Length (ft) of overflow structure acting as a sharp-crested Weir
Elevation of overflow structure to bypass inline sump (ft above sump base)

## Slide 21
Single Chamber Device Characteristics with Inflow Geometry Bypass Data
Defined Flow Diversion Geometry
Notes: Hydrodynamic devices are available for any individual source area. If you want to combine more than one source area, you can model the single chamber device as a catchbasin with inflow bypass data in the drainage system.
You will also need to enter either the information necessary to characterize a single chamber device or a proprietary device. The single chamber device includes the same information that you would enter for a catchbasin with inflow bypass data. The proprietary device option will allow you to select a particular device manufacturer and model number, assuming the performance data for that device has been added to WinSLAMM.
Single Chamber Device Characteristics. If you are modeling a generic single chamber device, you must enter the following information.
Average sump depth below hydrodynamic device outlet invert (feet)
Depth of sediment in hydrodynamic device sump at beginning of study period (ft)
Typical outlet pipe diameter (ft)
Typical outlet pipe Mannings n
Typical outlet pipe slope (ft/ft)
Typical hydrodynamic device sump surface area (square feet)
Total hydrodynamic device depth (feet)
Inflow hydrograph peak to average flow ratio
Maximum allowable depth of sediment below outlet invert elevation
Either: Maximum flow to inline sump (cfs)
Or: Diameter of orifice that controls flow to in-line sump (ft)
Inflow orifice invert elevation (ft)
Length (ft) of overflow structure acting as a sharp-crested Weir
Elevation of overflow structure to bypass inline sump (ft above sump base)

## Slide 22
Hydrodynamic Proprietary Device Information
Notes: Hydrodynamic devices are available for any individual source area. If you want to combine more than one source area, you can model the single chamber device as a catchbasin with inflow bypass data in the drainage system.
Proprietary Device. If you are modeling a proprietary device, check the 'Or Use Proprietary Hydrodynamic Control Device Information' checkbox and then use the pull down menu to select the device manufacturer and model number. Enter any other relevant information in the data grid.
Note that there are currently no proprietary devices available in the model. The devices will become available as the manufacturer supplies either regulatory agency or peer-reviewed performance data to us.

## Slide 23
Hydrodynamic Device Cleaning Information
Notes: Hydrodynamic devices are available for any individual source area. If you want to combine more than one source area, you can model the single chamber device as a catchbasin with inflow bypass data in the drainage system.
Device Cleaning. You may enter in either specific cleaning dates or a cleaning frequency. If you select to model device cleaning, then when the date in the model run is reached during processing, the program will remove all stored sediment in the device. Note than if you select a cleaning frequency of more than one year you will need to run a rainfall file that is longer than a year.

## Slide 24
Hydrodynamic Device with Lamella Plates or Settling Tubes
Notes: Model Hydrodynamic Device with Lamella Plates or Settling Tubes. This option allows you to model the increased settling efficiency that occurs when the device uses lamella plates or settling tubes. When you select this option, the program increases the effective surface area of the device by the number of plates or tubes that a vertical line will intersect. This occurs for each time step that the flow through the device is laminar. Laminar flow is assumed if the Reynolds number is less than 2100. The Reynolds number is determined from the water velocity through the tubes (and so varies with flow), the kinematic viscosity of the water, and the tube diameter or distance between lamella plates. For more information, see
To model a hydrodynamic device with lamella plates or settling tubes, first check the box next to the lamella plate or settling tube label. Then you must enter:
1. The fraction of the total device surface area (0 - 1) with plates or tubes.
2. The average settling tube diameter or distance between lamella plates (ft)
3. The number of plates or tubes a vertical line will intersect.

## Slide 25
Increase the effective surface area of the device by the number of times a vertical line crosses a plate or tube
What are Lamella Plates?
Key Variables
Fraction of device area with plates or tubes
Average tube diameter or distance between plates
Number of plates or tubes in a vertical line

## Slide 26
Detailed Output Options